## Slide 1
What Your Sensors Are Telling You
A year of climate data from the warehouse office
Netatmo sensors · 3 locations · 17,519 readings · 2025

## Slide 2
The Big Picture
Your office is comfortable — but the air gets stale in winter.
Temperature
20.1°C
Comfortable year-round (10.9–29.8°C)
Humidity
70%
Borderline — mould threshold is 60%
CO2
496 ppm
Fine on average — but 17 bad days
KEY INSIGHT
The building retains heat well, but CO2 builds up when windows are closed. Winter months (May–Sep) account for all 17 bad air quality days.

## Slide 3
Air Quality
CO2 spikes in winter evenings — when the building is sealed.
THE PROBLEM
11 events exceeded 800 ppm 54 total hours of poor air quality 9 events lasted longer than 3 hours Worst event: Aug 4–5 8.5 hours at peak 1,678 ppm All bad days happen May–Sept (winter, windows closed)
THE DAILY PATTERN
6:00
472 ppm
Best air — open windows
8:00
473 ppm
People arrive, CO2 starts rising
13:00
514 ppm
Peak CO2 — most occupied
18:00
500 ppm
People leave, CO2 falls
21:00
508 ppm
Risk zone if still occupied

## Slide 4
Humidity
70% average humidity is a year-round mould risk.
WHERE THE MOISTURE COMES FROM
Weather infiltration
43%
Morning condensation
29%
Occupancy
20%
Other
8%
WHEN IT'S WORST
Jun
65% of readings >75%
Jul
62% of readings >75%
Aug
58% of readings >75%
Sep
52% of readings >75%
May
48% of readings >75%
ACTION
Get a dehumidifier for Jun–Aug. Check for water ingress after storms. Consider humidity-resistant materials for design work.

## Slide 5
Building Performance
The building retains heat well — but airflow is the real story.
Thermal Mass
9 hours
Temperature half-life after people leave
Airflow
No lag
Air circulates freely between all 3 floors
Envelope
Moderate
Storms drop indoor temp 0.66°C over 12hrs
ENERGY PROFILE
Estimated annual heating: 2,059 kWh Heating degree-days: 858 Peak demand: August (6.5 HDD/day)
Kitchen runs 1–2°C warmer than other rooms year-round. Heating is concentrated there — other zones may be underheated in winter.

## Slide 6
People Patterns
The office is active 8am–9pm, with clear seasonal rhythms.
OCCUPANCY
Active window
08:00–21:00
Peak noise
3–4pm (54.7 dB)
Est. people
~7 average
Busiest month
February
Quietest month
May
Weekend activity
15.1 hrs/day
ANOMALIES & LEAVE
Anomalous days
203 detected
Worst anomaly
Mar 2 (noise z=7.5)
Peak leave
Mar–Apr (18 days)
Christmas
Dec 23–31 shutdown
Winter leave
Almost none
Busiest week
Jan 20 (post-holiday)

## Slide 7
What To Do
Three things that would make the biggest difference.
Ventilate smarter
→ Open windows at 6–7am (lowest CO2)
→ Open again after 5pm if staying late
→ In winter, crack a window when CO2 rises
Control humidity
→ Get a dehumidifier for Jun–Aug
→ Check for water ingress after storms
→ Use humidity-resistant storage for materials
Balance the heating
→ Kitchen runs 1–2°C hotter than other rooms
→ Consider zoning adjustments
→ The building retains heat well — use that

## Slide 8
The building is talking.
The sensors are listening.
Now you know what to do about it.
Full interactive dashboard and analysis available.